## Horizontal Vessel
[7 empty] | Client |  | Job
Unit
Plant
[9 empty] | Sheet |  | 1 | of | 1
PSV CALCULATION SHEET - FIRE CASE | [9 empty] | V. 1.0 by M.Meloni
1 | INPUT DATA
2 | Set pressure |  | kg/h | barg | 6 |  |  | Relief temperature | °C | 130
3 | Accumulation |  | kg/h | % | 21 |  |  | Latent heat | kcal/kg | 500
4 | Molecular weight |  |  | kg/kmol | 30 |  |  | Compressibility factor Z |  | 1
5 | Cp/Cv |  |  |  | 1.3 |  |  | Kd |  | 0.975
6 | Kb |  |  |  | 1 |  |  | Kc |  | 1
7 | Enviroment factor F |  |  |  | 1 |  |  | Good drainage/firefighting exists |  | YES
8 | Backpressure |  |  | barg | 0.35
9 | VESSEL DATA
10 | Diameter |  |  | m | 4 |  |  | Tank elevation | m | 5
11 | Lenght (TL - TL) |  |  | m | 7.5 |  |  | Additional % for piping | % | 10
12 | Maximum liquid level |  |  | m | 3.5
13
14
15 | [6 empty] | 7.5 | m
16
17
18
19
20
21 |  |  |  |  | 3.5 | m | 4 | m
22
23
24
25
26
27
28
29 |  | Ground | 5 | m
30
31
32
33
34 | CALCULATION
35 | Relief pressure |  |  | barg | 7.26 |  |  | Max liquid height subjected to fire | m | 2.6
36 | Fraction of head wetted |  |  |  | 0.68808
37 | Head wetted area (emisphere) |  |  | m2 | 21.9911 |  |  | TL-TL wetted area | m2 | 56.2647
38 | Pipe wetted area |  |  | m2 | 10.0247 |  |  | Total wetted area | m2 | 110.2717
39 | Heat absorbed |  |  | kcal/h | 1756462.6954 |  |  | Relief flowrate | kg/h | 3512.9254
40 | Critical pressure |  |  | bara | 3.8201 |  |  | Critical flow (sonic) |  | YES
41 | C parameter |  |  |  | 0.026344 |  |  | Minimum area if critical | mm2 | 606.9923
42 | r parameter |  |  |  | 0.19286 |  |  | F2 parameter |  | 0.36725
43 | Minimum area if not critical |  |  | mm2 | 1023.6565
44
45 | FINAL RESULTS
46
47 | Heat absorbed |  |  | kcal/h | 1756462.6954 |  |  | Minimum discharge area required | mm2 | 606.9923
48 | Total wetted area |  |  | m2 | 110.2717 |  |  |  | inch2 | 0.94084
49
50
51
52
53
54
55
56
57
58
59
60
61
62
To be used only for didactic purposes or preliminary estimation. Not to be used for definitive design of a PSV.
Note on W12: [Commento in thread] La versione di Excel in uso consente di leggere questo commento in thread, ma tutte le modifiche a esso apportate verranno rimosse se il file viene aperto in una versione più recente di Excel. Ulteriori informazioni: https://go.microsoft.com/fwlink/?linkid=870924 Commento: 0.975 if PSV, 0.62 if rupture disk
Note on W13: [Commento in thread] La versione di Excel in uso consente di leggere questo commento in thread, ma tutte le modifiche a esso apportate verranno rimosse se il file viene aperto in una versione più recente di Excel. Ulteriori informazioni: https://go.microsoft.com/fwlink/?linkid=870924 Commento: 0.9 if there is rupture disk + PSV, otherwise 1
Note on C14: [Commento in thread] La versione di Excel in uso consente di leggere questo commento in thread, ma tutte le modifiche a esso apportate verranno rimosse se il file viene aperto in una versione più recente di Excel. Ulteriori informazioni: https://go.microsoft.com/fwlink/?linkid=870924 Commento: Typical values: If unknown or bare vessel: 1 If there are depressurizing facilities: 1 If there are water application facilities on the bare vessel: 1 If insulated (Conductance<20 W/m2k during fire): 0.3 If insulated (Conductance<5.67 W/m2K during fire): 0.075 If vessel is covered with earth: 0.03

## Horizontal Vessel with boot
[7 empty] | Client |  |  |  |  | Job
Unit
Plant
[12 empty] | Sheet |  |  | 1 | of | 1
PSV CALCULATION SHEET - FIRE CASE | [13 empty] | V. 1.0 by M.Meloni
1 | INPUT DATA
2 | Set pressure |  | kg/h | barg | 6 |  |  | Relief temperature |  |  |  | °C |  | 130
3 | Accumulation |  | kg/h | % | 21 |  |  | Latent heat |  |  |  | kcal/kg |  | 500
4 | Molecular weight |  |  | kg/kmol | 30 |  |  | Compressibility factor Z | [5 empty] | 1
5 | Cp/Cv |  |  |  | 1.3 |  |  | Kd | [5 empty] | 0.975
6 | Kb |  |  |  | 1 |  |  | Kc | [5 empty] | 1
7 | Enviroment factor F |  |  |  | 1 |  |  | Good drainage/firefighting exists | [5 empty] | YES
8 | Backpressure |  |  | barg | 0.35
9 | VESSEL DATA
10 | Diameter |  |  | m | 4 |  |  | Tank elevation |  |  |  | m |  | 5
11 | Lenght (TL - TL) |  |  | m | 7.5 |  |  | Additional % for piping |  |  |  | % |  | 10
12 | Maximum liquid level |  |  | m | 3.5 |  |  | Boot height |  |  |  | m |  | 0.5
13 | Boot diameter |  |  | m | 0.5
14
15 | [6 empty] | 7.5 | m
16
17
18
19
20
21 |  |  |  |  | 3.5 | m | 4 | m
22
23
24
25
26 | [8 empty] | 0.5 | m
27 | [10 empty] | 0.5 |  | m
28
29 |  | Ground | 5 | m
30
31
32
33
34 | CALCULATION
35 | Relief pressure |  |  | barg | 7.26 |  |  | Max liquid height subjected to fire |  |  |  | m |  | 2.6
36 | Fraction of head wetted |  |  |  | 0.68808
37 | Head wetted area (emisphere) |  |  | m2 | 21.9911 |  |  | TL-TL wetted area |  |  |  | m2 |  | 56.2647
38 | Pipe wetted area |  |  | m2 | 10.0247 |  |  | Boot area |  |  |  | m2 |  | 1.1781
39 | Heat absorbed |  |  | kcal/h | 1771835.5302 |  |  | Total wetted area |  |  |  | m2 |  | 111.4498
40 | Critical pressure |  |  | bara | 3.8201 |  |  | Relief flowrate |  |  |  | kg/h |  | 3543.6711
41 | C parameter |  |  |  | 0.026344 |  |  | Critical flow (sonic) | [5 empty] | YES
42 | r parameter |  |  |  | 0.19286 |  |  | Minimum area if critical |  |  |  | mm2 |  | 612.3048
43 | Minimum area if not critical |  |  | mm2 | 1032.6157 |  |  | F2 parameter | [5 empty] | 0.36725
44
45 | FINAL RESULTS
46
47 | Heat absorbed |  |  | kcal/h | 1771835.5302 |  |  | Minimum discharge area required |  |  |  | mm2 |  | 612.3048
48 | Total wetted area |  |  | m2 | 111.4498 | [6 empty] | inch2 |  | 0.94907
49
50
51
52
53
54
55
56
57
58
59
60
61
62
To be used only for didactic purposes or preliminary estimation. Not to be used for definitive design of a PSV.
Note on W12: [Commento in thread] La versione di Excel in uso consente di leggere questo commento in thread, ma tutte le modifiche a esso apportate verranno rimosse se il file viene aperto in una versione più recente di Excel. Ulteriori informazioni: https://go.microsoft.com/fwlink/?linkid=870924 Commento: 0.975 if PSV, 0.62 if rupture disk
Note on W13: [Commento in thread] La versione di Excel in uso consente di leggere questo commento in thread, ma tutte le modifiche a esso apportate verranno rimosse se il file viene aperto in una versione più recente di Excel. Ulteriori informazioni: https://go.microsoft.com/fwlink/?linkid=870924 Commento: 0.9 if there is rupture disk + PSV, otherwise 1
Note on C14: [Commento in thread] La versione di Excel in uso consente di leggere questo commento in thread, ma tutte le modifiche a esso apportate verranno rimosse se il file viene aperto in una versione più recente di Excel. Ulteriori informazioni: https://go.microsoft.com/fwlink/?linkid=870924 Commento: Typical values: If unknown or bare vessel: 1 If there are depressurizing facilities: 1 If there are water application facilities on the bare vessel: 1 If insulated (Conductance<20 W/m2k during fire): 0.3 If insulated (Conductance<5.67 W/m2K during fire): 0.075 If vessel is covered with earth: 0.03

## Vertical Vessel
[8 empty] | Client |  |  |  |  | Job
Unit
Plant
[13 empty] | Sheet |  | 1 | of | 1
PSV CALCULATION SHEET - FIRE CASE | [13 empty] | V. 1.0 by M.Meloni
1 | INPUT DATA
2 | Set pressure |  | kg/h | barg | 6 |  |  |  |  | Relief temperature |  |  | °C | 130
3 | Accumulation |  | kg/h | % | 21 |  |  |  |  | Latent heat |  |  | kcal/kg | 500
4 | Molecular weight |  |  | kg/kmol | 30 |  |  |  |  | Compressibility factor Z |  |  |  | 1
5 | Cp/Cv |  |  |  | 1.3 |  |  |  |  | Kd |  |  |  | 0.975
6 | Kb |  |  |  | 1 |  |  |  |  | Kc |  |  |  | 1
7 | Enviroment factor F |  |  |  | 1 |  |  |  |  | Good drainage/firefighting exists |  |  |  | YES
8 | Backpressure |  |  | barg | 0.35
9 | VESSEL DATA
10 | Diameter |  |  | m | 4 |  |  |  |  | Tank elevation |  |  | m | 5
11 | Height (TL - TL) |  |  | m | 7.5 |  |  |  |  | Additional % for piping |  |  | % | 10
12 | Maximum liquid level |  |  | m | 3.5
13
14
15
16
17
18
19
20
21 |  |  |  |  | 3.5 | m |  |  |  |  | 7.5 | m
22
23 | [6 empty] | 4 |  | m
24
25
26
27
28
29 |  | Ground | 5 | m
30
31
32
33
34 | CALCULATION
35 | Relief pressure |  |  | barg | 7.26 |  |  |  |  | Max liquid height subjected to fire |  |  | m | 2.6
36 | Head wetted area |  |  | m2 | 25.1327
37 | Pipe wetted area |  |  | m2 | 5.7805 |  |  |  |  | TL-TL wetted area |  |  | m2 | 32.6726
38 | Heat absorbed |  |  | kcal/h | 1118340.4261 |  |  |  |  | Total wetted area |  |  | m2 | 63.5858
39 | Critical pressure |  |  | bara | 3.8201 |  |  |  |  | Relief flowrate |  |  | kg/h | 2236.6809
40 | C parameter |  |  |  | 0.026344 |  |  |  |  | Critical flow (sonic) |  |  |  | YES
41 | r parameter |  |  |  | 0.19286 |  |  |  |  | Minimum area if critical |  |  | mm2 | 386.4722
42 | Minimum area if not critical |  |  | mm2 | 651.7625 |  |  |  |  | F2 parameter |  |  |  | 0.36725
43
44
45 | FINAL RESULTS
46
47 | Heat absorbed |  |  | kcal/h | 1118340.4261 |  |  |  |  | Minimum discharge area required |  |  | mm2 | 386.4722
48 | Total wetted area |  |  | m2 | 63.5858 | [7 empty] | inch2 | 0.59903
49
50
51
52
53
54
55
56
57
58
59
60
61
62
To be used only for didactic purposes or preliminary estimation. Not to be used for definitive design of a PSV.
Note on W12: [Commento in thread] La versione di Excel in uso consente di leggere questo commento in thread, ma tutte le modifiche a esso apportate verranno rimosse se il file viene aperto in una versione più recente di Excel. Ulteriori informazioni: https://go.microsoft.com/fwlink/?linkid=870924 Commento: 0.975 if PSV, 0.62 if rupture disk
Note on W13: [Commento in thread] La versione di Excel in uso consente di leggere questo commento in thread, ma tutte le modifiche a esso apportate verranno rimosse se il file viene aperto in una versione più recente di Excel. Ulteriori informazioni: https://go.microsoft.com/fwlink/?linkid=870924 Commento: 0.9 if there is rupture disk + PSV, otherwise 1
Note on C14: [Commento in thread] La versione di Excel in uso consente di leggere questo commento in thread, ma tutte le modifiche a esso apportate verranno rimosse se il file viene aperto in una versione più recente di Excel. Ulteriori informazioni: https://go.microsoft.com/fwlink/?linkid=870924 Commento: Typical values: If unknown or bare vessel: 1 If there are depressurizing facilities: 1 If there are water application facilities on the bare vessel: 1 If insulated (Conductance<20 W/m2k during fire): 0.3 If insulated (Conductance<5.67 W/m2K during fire): 0.075 If vessel is covered with earth: 0.03

## GUIDE AND LICENCE
GUIDE
This excel file allows the calculation of the fire case for a preliminary sizing of a pressure safety valve (PSV) or rupture disk, in critical (sonic) of subcritical (non sonic) conditions.
The file can calculate the wetted area of a vessel for the following cases:
1) Horizontal vessel
2) Horizontal vessel with boot
3) Vertical vessel
All of them having a separated Calculation sheet page sized to be printed in a A4 page.
Limitations
- The program don't handle liquid or byphase fluids.
- Vessel heads are assumed emispheric. For this reason, the wetted area calculated could be overestimated.
- Vessel is assumed without internals.
- Heat dispersion and transitories are not calculated.
- At the moment, the program don't have any knowledge of the fluid characteristics input by the user, in particular, steam is calculated with the general formula used for gas.
Given the above limitations, the program must not be used to do a detailed or definitive design of a PSV.
THE PROGRAM IS FREE TO USE AND PROVIDED “AS IS”, WITHOUT WARRANTY OF ANY KIND, EXPRESS OR IMPLIED, INCLUDING BUT NOT LIMITED TO THE WARRANTIES OF MERCHANTABILITY, FITNESS FOR A PARTICULAR PURPOSE AND NONINFRINGEMENT.
IN NO EVENT SHALL THE AUTHOR BE LIABLE FOR ANY CLAIM, DAMAGES OR OTHER LIABILITY, ARISING FROM, OUT OF OR IN CONNECTION WITH THE SOFTWARE OR THE USE OR OTHER DEALINGS IN THE SOFTWARE.
THE ENTIRE RISK ARISING OUT OF USE OR PERFORMANCE OF THE PROGRAM REMAINS WITH YOU.
How to use
In order to use the spreadsheets, all the |  | cells must be filled by the user.
The | cells shows intermediate calculations done by the program. These cells must not be modified by the user.
The | cells shows the final results after the calculation steps with indication of the heat load generated and the minimum orifice area required to discharge the flow calculated.
Also those cells must not be modified by the user.
The | cells are further divided in two section.
The first, "INPUT DATA", includes the fluid properties (molecular weight, cp/cv, latent heat…), discharge conditions (backpressure, accumulation pressure…) and parameters used in the API formulas (Kd, Kc, Enviroment factor...).
For details, please refer to API 520 and API 521 last edition.
The second section, "VESSEL DATA", includes the vessel dimensions.
In order to account for piping around the vessel, use the "Additional % for piping" cell.